## Compiled All
Annexure A- Tender No - 001/CRRAO/NSM/25-26/05-01
Name of Bidder - Network Techlab India Limited
Sr. | Section / Page/ Clause Reference | Query from bidder | CR RAO AIMSCS Response
1 | General | Technical bid to be submitted online & Commercial Bid to be submitted offline at AIMSCS location. Kindly confirm. | Technical bids to be submitted in soft copy on info_nsm@crraoaimscs.res.in and commerical to be submitted in sealed enevalop as per tender schedule provided.
2 | 12.6 / Pg 11 / Evalualation of Bid | Request you to consider CDCP/CDCS for evaluation. Seperate Weightage only to ATD we request you to kindly amend. | As per Tender
3 | 2 Background / Pg 21 / All compute Racks are not part of the scope of this Bid whereas storage rack and spare rack each of 45 U are scope of this tender. | This line item is missing in the price bid BOQ. Should we consider the cost under - 17. Any other item, material required to complete the solution? | Refer Corrigendum
4 | 6 Requirements towards Civil / Pg 25 / 6.4.2 Pedestal installed to support the panel will be suitable to achieve a finished floor height of 400mm. | Please confirm raised floor height will be 400mm or 300mm as per secton layout provided. | Raised floor height is 300 mm
5 | 6 Requirements towards Civil / Pg 25 / 6.5 Fire Rated Steel Door-two hours | Please confirm MS FR door to be considered for Server room main entry. Since in section drawing Server Room main door shown is FR Glass door. Cabin Door entry will be glass door non-fr as asked. | Server room main door should fire rated MS
6 | 7 Requirements towards Electrical / Pg 27 / 7.2 Existing change over panel needs to be removed and new panel | During C/O panel replacement, shutdown would be required wherein existing LT panel would be debarred from EB or DG supply. | Yes shut down will be provided. Bidder to submit along with Bid the duriation of shut down
7 | 7 Requirements towards Electrical / Pg 36 / 7.6.2 UPS with backup time of 10 Mins at Unity PF with END of life 10 years | Kindly confirm IT UPS LIB to be designed at Unity PF for 10 mins & Non-IT SMF to be designed for 10 mins @70KVA as per BOQ. | Refer Tender clause no 7.6.2 as " A Battery system shall be furnished for the UPS with backup time of 10 Mins at Unity PF with END of life 10 years ( Warranty should be of 10 years), capacity to maintain UPS output at the specified load for the duration. " and for NON IT UPS Power factor to be considered as 0.9 lag
8 | 7 Requirements towards HVAC / Pg 56 / 8.10 Piping from Adiabatic Dry cooler to CDU and piping inside server room should be grooved with grooved joints as per below specification | In layout CDU location is not shown. Kindly confirm till where the piping with GC to be given inside the server room. | Piping should be as per layout drawing provided . Location of CDU will be in two rack - Rack 1 and rack-2
9 | 7 Requirements towards HVAC / Pg 59 / 8.18 Water Storage Tank for Adiabatic Purpose- SMC Panel tank for Water storage purpose on rooftop | From where the water inlet tapping point for 7500 L Water Tank of Adiabatic Dry Cooler to be taken? | Adiabatoc water tank should be on ground and needs to tap from exisiting nearest line . Bidder to consider U PVC pipe for same along with all accessroeies as valve,isolator ,coupling ,joints, Bidder to consider approxmate length of this pipw as 30 meters.
10 | 9 Requirements towards IBMS / Pg 59 / 9.5 The objective is to protect the entire premises viz. server area, utility area etc., all the voids against rodents | For Rodent System, apart from server room & ups room it is also asked for the utility area. Is this the existing panel room where New C/O panel would be installed? | Rodent system to be required in Server room and UPS and Battery room.
11 | 9 Requirements towards IBMS / Pg 64 / 9.7 Supply and implementing NOVEC 1230 | Fire Suppression cylinders shown in the layout is on the exterior side of the building which will be open to the ambience. Challenge since the cylinders are designed at 24-27 degC. | As per NFPA 72 guidelines
12 | 9 Requirements towards IBMS / Pg 64 / 9.7 Suppression system needs to be inside the server rack as system is with close containment and in UPS and battery room needs to be for full room. | Tender asks for Hot Aisle whereas if for server room only containment area to be considered then due to racks having perforated door it will be challenging to only consider close containment. Volume consideration to be full room for system to be effective. Else should have both Cold & Hot Aisles for closed containment. | As per drawing provided . Drawing are provided with only Hot aisel containtement . Gas supression system needs to be considered for entire server area and entire UPS and Battery area.
Name of Bidder - Vertiv Energy Pvt Limited
Sr. | Section / Page/ Clause Reference | Query from bidder | CR RAO AIMSCS Response
1 | Page 29 of 96 7.5 Modular UPS for IT as well as NON IT Load:- 1.UPS for IT Load with Li-ION batteries for 10 minutes back up time of rating 150 KVA (Module Size should be 25 KW to 60 KW) | Kindly amend as : 7.5 Modular UPS for IT as well as NON IT Load:- 1.UPS for IT Load with Li-ION batteries for 10 minutes back up time of rating 150 KVA sclable to 300kVA (Module Size should be 25 KW to 60 KW) | As per Tender
2 | Page 29 of 96 2. 1 X 75 KVA UPS for NON-IT Load – Utiliy Load with SMF batteries for 10 minutes back up time 0n 75 KVA. | Kindly amend as : 2. 1 X 75 KVA UPS scalable to 120 kVA for NON-IT Load – Utiliy Load with SMF batteries for 10 minutes back up time on 75 KVA. | As per Tender
3 | Page 29 of 96 7.5.2 The UPS shall be housed in a freestanding cabinet with casters and shall contain Static Bypass and maintenance Bypass isolator. | Kindly amend as : The UPS shall be housed in a freestanding cabinet with casters / base frame or levelling feet and shall contain Input , output ,Static Bypass and maintenance Bypass isolator. | As per Tender. For IT load UPS bypass needs to be disabled as IT load can not be operated on bypass. For NON IT UPS static and maintenance bypass are required.
4 | All serviceable components to be from front. Rear space upto 200mm can be provided only for ventilation purpose UPS display should show the battery status monitoring, UPS mode, Alarm (Audio and visible), Events etc. | All serviceable components to be from front. Rear space upto 500mm can be provided only for ventilation purpose UPS display should show the battery status monitoring, UPS mode, Alarm (Audio and visible), Events etc. | It is provided , Refer drawings given.
5 | Page 30 of 96 7.5.7 The UPS shall be designed for forced air cooling. Air inlets shall be provided from the front. Air exhaust shall be from the top portion of the unit or from back side with maximum space available up to 200mm. | Kindly amend as : 7.5.7 The UPS shall be designed for forced air cooling. Air inlets shall be provided from the front. Air exhaust shall be from the top portion of the unit or from back side with maximum space available up to 500mm. | Refer drawing provided
6 | Page 30 of 96 7 Requirements towards Electrical Work - 7.5 Modular UPS for IT as well as NON IT Load:- 7.5.9 STANDARDS - Product should confirm to below minimum applicable standards : IEC 62040-3 UPS PERFORMANCE, IEC 60950, CE, VDE, UL 1778 for UPS | Kindly amend as : 7.5.9 STANDARDS Product should confirm to below minimum applicable standards : IEC EN 62040-1-2 general & safety req; IEC EN62040-2 EMC requirements; IEC EN62040-3 operating requirements; Surge withstandability EN61000-4-5, level3 | Accepted
7 | Page 31 of 96 Output connectors :Three phase: Hardwire 5-wire (3 Phase + N + G) | Kindly amend as : Output connectors :380/400/415 (three-phase four-wire, with neutral reference to the bypass neutral) | As per Tender
8 | Page 32 of 96 7.5.12 ENVIRONMENTAL Phase sequence correction : Required | Kindly amend as : 7.5.12 ENVIRONMENTAL Phase sequence correction : Required , UPS should continue to work on main supply without switching to battery . | Phase sequence correction is not required
9 | Page 38 of 96 7.6.4 Batteries should be compliant to Safety Cell: UL1642 Module :UL 1973 Transportation : UN38.3 Seismic :GR63 EMC : IEC61000-6-2, and 61000-6-4 Rack Level : UL 1998,991 Battery Module & Switchgear : UL 1973 with each component level battery Aging factor : IEEE 495 Battery manufacturer should have Quality Certificate : (i) ISO 14001:2004 (Environment) & OHSAS 18001:2007 (Health & Safety) and (ii) ISO 9001-2008 | Kindly amend as : 7.6.4 Batteries should be compliant to below or equivalent standards : Safety Cell: UL1642 Module :UL 1973 Transportation : UN38.3 Seismic :GR63 EMC : IEC61000-6-2, and 61000-6-4 Rack Level : UL 1998,991 Battery Module & Switchgear : UL 1973 with each component level battery Aging factor : IEEE 495 Battery manufacturer should have Quality Certificate : (i) ISO 14001:2004 (Environment) & OHSAS 18001:2007 (Health & Safety) and (ii) ISO 9001-2008 | Accepted
10 | Page 38 of 96 7.6.4 Batteries should be compliant to | Kindly add UL 9540 for fire Safety considering data centre application . | Accepted
11 | Page 45 of 96 / 8.5 DX Based In Row Unit - Filters - Filter to be provided on the Package unit, having 95% efficiency down to 5 Microns | Kindly amend as : Filters - G4 rated air filters following with EU4 to be provided on the Package unit having 90% efficiency down to 10 Microns | Accepted
12 | Page 46 of 96 / 8.5 DX Based In Row Unit - 8.5.1 The frame of the units is constructed of 16-gauge formed steel for maximum strength. | The frame of the units is constructed of 16 to 18 gauge formed steel for maximum strength | As per OEM standard manufactring practice
13 | Page 46 of 96 / 8.5 DX Based In Row Unit - The footprint of 300 mm is required | The footprint of 600 mm is required. | As per tender
14 | Page 47 of 96 / 8.5 DX Based In Row Unit - 8.5.3 Condensate Pump - : A condensate pump is factory wired and piped internally to the condensate drain pan. Within the condensate pump, there should be dual position float. The first position is used for condensate pump control and the other float generates a condensate pump failure alarm to prevent condensate pan overflow. | 8.5.3 Condensate Pump - : A condensate pump is factory wired and piped internally to the condensate drain pan . Within the condensate pump, there should be position float used for condensate pump control and to generates a condensate pump failure alarm to prevent condensate pan overflow. | Accepted
15 | Page 47 of 96 / 8.5 DX Based In Row Unit - 8.5.5 Electric heaters-Each packaged In Row unit shall be provided with multi stage heating elements constructed from aluminium. | 8.5.5 Electric heaters-Each packaged In Row unit shall be provided with single / multi stage heating elements constructed from aluminium. | As per OEM standard manufactring practice
16 | Page 47 of 96 8.5.9 Condenser Condenser with compressor inside is also recommended requirement as keeping compressor in the ODU unit (i.e. away from data center) will ease during routine maintenance as well as shut down maintenance activity and it lowers the sound level in Data Center. | Kindly accept compressor inside the indoor unit. | Accepted
17 | Page 47 of 96 8.5.12 De-humidification cycle shall operate by keeping the airflow constant but with the help of EEV to reduce the ADP of the coil. | 8.5.12 De-humidification cycle shall operate by variable airflow or with the help of EEV to reduce the ADP of the coil | Accepted
18 | Page 49 of 96 EXPANSION VALVE : 3. Dual Power supply. (RAW + UPS) | Kindly elaborate Dual Power supply. (RAW + UPS) asked for EEV | Single Power Supply is accepted
19 | Page 7 3.Eligibility Criteria | Kindly add below in OEM Eligibility Criteria in the bid : Critical Components asked in the RFP requirement i.e Rack with DC power distribution system , Inrow Cooling & UPS System must be from same & single OEM. | As per Tender
Name of Bidder - Schneider Electrical IT Business India Pvt Limited
Sr. | Section / Page/ Clause Reference | Query from bidder | CR RAO AIMSCS Response
1 | page 21/clause 2 BMS monitoring of CDU | Pls let us know total how many soft points to be considerde as well as what type of communication protocol between CDU to BMS | MODBUS SNMP - 35 nos of soft IO to be considered per CDU
2 | page 54/96 split units for UPS/Battery room | wall mounted split units of 11 kw (3.127 TR) may not be available with OEM's. Kindly review and modify the ratings | As per Tender
3 | page 59/96 water storage tanks -SMC Panel construction | Kindly review the requirement of 8000 liters also is it possible to go for multiple cylindrical tanks of say 4kLiters | We prefer to go with single tank , however bidder can choose between 1 X 8000 liters or 2 X 4000 liters
4 | 8.5.16 Type of Compressor | We have proposed Inverter scroll compressor, Requirement is showing Fixed compressor and technical spec in the Pg 46/ 8.5.2 Inverter Scroll Compressor is asked, need clarification on the same. | There is no fixed compresso , it is inverter with variable flow
5 | 8.5.16 Design condition | please let us know ambient temperature need to be consider. | As per ASHRAE n=20
6 | Section III Clause 2, Page 15 Project Timeline | We request to extend the Project Timeline from 4 months to 5months | As per Tender
7 | Section III Clause 17, Page 19 Limitation of Liability | We request you to modify the clause as below: "Notwithstanding anything to the contrary, the liability of the Bidder / Contractor arising out of breach of any terms/conditions of the tender / contract/work order and addendums/amendments thereto, misconduct, willful default will be limited to the total contract value. However, liability of the bidder in case of death/injury/damage caused to the personnel/property due to/arising out of/incidental to any act/omission/default/deficiency of bidder/contractor will be at actual. In no event shall either Party, its officers, directors, or employees be liable for any form of incidental, consequential, indirect, special or punitive damages of any kind" | ok
8 | Section III Clause 4, Page 15 Payments | We request you to provide an advance of 20% against the submission of Advance Bank Guarantee | As per Tender
9 | Section V, Page 76 Price Schedule | We request you to allow us to submit a detailed billing Annexure, which will not violate the Price Schedule. The intention is further break down the line items of the Price Schedule, in order to comply with the statutory GST invoicing requirements. | As per Tender
10 | Section III Clause 9, Page 17 Penalties | Please incorporate the following part “the penalties shall be levied for the reasons solely attributable to bidder” and we request prior notice shall be given to bidder with valid reason before levying | As per Tender
11 | Section III Clause 10, Page 18 Force Majeure | Please include Epidemic as a Force Majeure event. | As per Tender
12 | Section III Clause 13, Page 18 Indemnity | The successful bidder shall indemnify, protect and save C-DAC Pune from/against all claims, losses, costs, damages, expenses, action suits and other proceeding, resulting from/arising out of: 1. Infringement of any law pertaining to intellectual property, patent, trademarks, copyrights etc. by the bidder or 2. Such other statutory infringements by the bidder or caused by the sole reason attributed to the bidder, in respect of all the equipment’s supplied by successful bidder, or 3. Caused due to Intentional any act/omission/performance/under or non or part performance/failure of the bidder due to its negligence. | As per Tender
13 | Section III Clause 16, Page 19 Termination | Please amend as "The successful bidder may suspend or terminate the contract by at least 30 days’ written notice, only in the event of non-payment of undisputed invoices beyond 90 days from the due date or in the case of delay or default by the Buyer/ CR RAO AIMSCS in providing encumbrances free site fronts or right to access site or approach road to site." | As per Tender
14 | Section III Additional Clause Variation/Change Management | Either Party shall have the right to propose changes to the other Party that are considered necessary or desirable to improve the quality, efficiency or safety of the works agreed under the Contract. Any change upto +/- 10% of the Contract Price (this excludes items covered under price variation clause) may be considered at the agreed Price/ Rates with necessary time extension. However, in case of any change beyond 10%, the same shall be subject to acceptance of revised prices and delivery period proposed by the Contractor. The change shall be binding upon mutual acceptance by both the Parties in writing. | As per Tender
15 | Section III Additional Clause Extension of time | We request you to incorporate the following: Contractor shall be entitled for extension of time for completion without imposition of liquidated damages under following conditions, • Change in the Scope • Any occurrence of Force Majeure • Any suspension order given by the Employer • Any changes in laws and regulations • Any default or breach of the Contract by the Employer • Any delay on the part of a Subcontractor, provided such delay is due to a cause for which the Contractor himself would have been entitled to an extension of time • Delays attributable to the Employer • Any other delay beyond the reasonable control of the Contractor including but not limited to Force Majeure | As per Tender
16 | Section III Clause 1 Price variation | Please accept that the contractor shall have the right to vary the price in case of delay not attributable to the contractor. The basis of such escalations/price revision shall be on the basis of the IEEMA formula/RMI index and/or labour indices/Foreign exchange movement. | As per Tender
17 | Section II Additional Clause COVID-19 | We request you to accept: "All or part of the products and/or the services to be delivered and/or performed, according to the present offer/contract (“Supplies”) are produced, delivered, performed in, and/or sourced from areas that are or may become affected by the COVID-19 pandemic (including variants) and/or a shortage or interruption or delay in the transportation or procurement of raw materials, power and/or components ( “Circumstances”).Such Circumstances, even if known at the time of issuing or signing the present offer/contract, may trigger stoppage, hindrance or delays in the Vendor’s ability to produce, deliver, perform and/or source the Supplies. Consequently, notwithstanding any other provision of the contract or order" | As per Tender
18 | Section II Additional Clause Order of Precedence | We request you to incorporate the order of precedence as "The documents forming the Contract are to be taken as mutually explanatory of one another. For the purpose of interpretation, the priority of the documents shall be in accordance with the following sequence: a) The Contract Agreement b) The Letter of Award c) Minutes of Meeting d) Contractor’s Offer e) General Conditions of Contract f) Schedules & Annexures g) The Technical Specifications If any ambiguity or discrepancy arises or round in the documents, the same shall be mutually resolved between the Parties." | As per Tender
19 | Section II Additional Clause Effective date of the Contract | Please accept that: "The Contract shall come into force the day when all the following conditions are met: • Agreement / Contract document duly signed by the authorized representatives of both the Parties. • The agreed full advance payment has been received by the Contractor. • Full access and possession granted to Contractor for site activities. • A kick-off meeting between CDAC & Contractor held and minutes of meeting distributed on fulfilment of above conditions, CDAC shall issue a Notice to Proceed (“NTP”) to the Contractor, which shall be the Work Starting Date and be construed as Zero (0) date of the agreed schedule. NTP shall be issued only after the completion date of the last conditions (of milestone) from the above conditions. However, the coming into force shall occur within one month of the effective date of the Contract" | As per Tender
20 | Section II Additional Clause Export & Re-export Compliance | We request you to accept: The deliverables provided by Contractor under this Contract contain or may contain components and/or technologies from the United States of America (“US”), the European Union (“EU”) and/or other nations. CDAC acknowledges and agrees that the supply, assignment and/or usage of the products, software, services, information, other deliverables and/or the embedded technologies (hereinafter referred to as “Deliverables”) under this Contract shall fully comply with related applicable US, EU and other national and international export control laws and/or regulations. Unless applicable export license/s has been obtained from the relevant authority and the Contractor has approved, the Deliverables shall not (i) be exported and/or re -exported to any destination and party (may include but not limited to an individual, group and/or legal entity) restricted by the applicable export control laws and/or regulations; or (ii) be used for those purposes and fields restricted by the applicable export control laws and/or regulations. CDAC also agrees that the Deliverables will not be used either directly or indirectly in any rocket systems or unmanned air vehicles; nor be used in any nuclear weapons delivery systems; and will not be used in any design, development, production or use for any weapons which may include but not limited to chemical, biological or nuclear weapons. If any necessary or advisable licenses, authorizations or approvals are not obtained, whether arising from inaction by any relevant government authority or otherwise, or if any such licenses, authorizations or approvals are denied or revoked, or if the applicable export control laws and/or regulations would prohibit Contractor from fulfilling any order, or would in Contractor’s judgment otherwise expose Contractor to a risk of liability under the applicable export control laws and/or regulations if it fulfilled the order, | As per Tender
21 | Section II Additional Clause Purchaser’s Cybersecurity Obligations | We request you to accept: "Purchaser’s Obligations for Its Systems: Purchaser is solely responsible for the implementation and maintenance of a comprehensive security program (“Security Program”) that contains reasonable and appropriate security measures and safeguards to protect its computer network, systems, machines, and data (collectively, “Systems”), including those Systems on which it runs the Products or which it uses with the Services, against Cyber Threats. “Cyber Threat” means any circumstance or event with the potential to adversely impact, compromise, damage, or disrupt Purchaser’s Systems or that may result in any unauthorized access, acquisition, loss, misuse, destruction, disclosure, and/or modification of Purchaser’s Systems, including any data, including through malware, hacking, or similar attacks. Without limiting the foregoing, Purchaser shall at a minimum: (a) have qualified and experienced personnel with appropriate expertise in cybersecurity maintain Purchaser’s Security Program, and have such personnel regularly monitor cyber intelligence feeds and security advisories applicable to Purchaser’s Systems or Purchaser’s industry; (b) promptly update or patch its Systems or implement other appropriate measures based on any reported Cyber Threats and in compliance with any security notifications or bulletins, whether publicly disclosed on SE’s security notification webpage at https://www.se.com/ww/en/work/support/cybersecurity/security-notifications.jsp or otherwise provided to Purchaser; (c) regularly monitor its Systems for possible Cyber Threats; (d) regularly conduct vulnerability scanning, penetration testing, intrusion scanning, and other cybersecurity testing on its Systems; and (e) meet the recommendations of SE’s Recommended Cybersecurity Best Practices, available at https://www.se.com/us/en/download/document/7EN52-0390/, as may be updated by SE from time to time, and then-current industry standards. Purchaser’s Use of the Products, Software, and Services: SE may release Updates and Patches for its Products, Software, and Services from time to time. Purchaser shall promptly install any Updates and Patches for such Products, Software, or Services as soon as they are available in accordance with SE’s installation instructions and using the latest version of the Products or Software, where applicable. An "Update" means any software that contains a correction of errors in a Product, Software, or Service and/or minor enhancements or improvements for a Product, Software, or Service, but does not contain significant new features. A “Patch” is an Update that fixes a vulnerability in a Product, Software, or Service. Purchaser understands that failing to promptly and properly install Updates or Patches for the Products, Software, or Services may result in the Products, Software, or Services or Purchaser’s Systems becoming vulnerable to certain Cyber Threats or result in impaired functionality, and SE shall not be liable or responsible for any losses or damages that may result. Identification of Cyber Threats: If Purchaser identifies or otherwise becomes aware of any vulnerabilities or other Cyber Threats relating to the Products, Software, or Services for which SE has not released a Patch, Purchaser shall promptly notify SE of such vulnerability or other Cyber Threat(s) via the SE Report a Vulnerability page (https://www.se.com/ww/en/work/support/cybersecurity/report-a-vulnerability.jsp#Customers) and further provide SE with any reasonably requested information relating to such vulnerability (collectively, “Feedback”). SE shall have a non-exclusive, perpetual and irrevocable right to use, display, reproduce, modify, and distribute the Feedback (including any confidential information or intellectual property contained therein) in whole or part, including to analyze and fix the vulnerability, to create Patches or Updates for its customers, and to otherwise modify its Products, Software, or Services, in any manner without restrictions, and without any obligation of attribution or compensation to Purchaser; provided, however, SE shall not publicly disclose Purchaser’s name in connection with such use or the Feedback (unless Purchaser consents otherwise). By submitting Feedback, Purchaser represents and warrants to SE that Purchaser has all necessary rights in and to such Feedback and all information it contains, including to grant the rights to SE described herein, and that such Feedback does not infringe any proprietary or other rights of third parties or contain any unlawful information" | As per Tender
22 | Section III Clause 16, Page 19 Termination | We request you to add the underlined part of the sentence as below: "CR RAO AIMSCS will release the due amount payable to successful bidder towards the material and / or services provided till the date of termination, those are accepted by CR RAO AIMSCS, including the confirmed orders." | As per Tender
23 | Section III Clause 16, Page 19 Termination | We request you to add the following part of the sentence as below: "The contractor shall also be entitled for payment with reasonable profit by CDAC on the part of the terminated works; Payment of a sum representing 10% of the contract price as a termination fee" | As per Tender
24 | Section III Additional Clause Additional requirements | For any additional or new work/ requirement, Contractor shall evaluate the physical, technical schedule and cost impacts before giving acceptance to the same. However, such work shall be carried out on Cost plus basis which shall be charged Cost + Overheads + 25% Profit margin. | As per Tender
25 | Section III Clause 11, Page 16 of 52 Risk and Ownership | Please modify as : "All risks, responsibilities, and liabilities in respect of goods delivered at site shall remain with selected bidder till they are successfully installed and commissioned at site and taken over by end users. Part deliveries shall not be treated as deliveries. Only full deliveries of all items ordered will be considered as delivery. The ownership of the items delivered at site, shall be of C-DAC Pune on successful installation of items" | As per Tender
26 | Section III Clause 15 Suspension | Please add the below to the clause: "If the CR RAO AIMSCS/Buyer fails to comply with the provisions of this Contract, the Successful bidder/ Seller may, after giving not less than 14 days' notice to the Buyer, suspend work or reduce the rate of work. If the Buyer subsequently cures the failure as specified in the notice, the Seller shall resume normal working as soon as is reasonably practicable. If the Seller suffers delay and/or incurs Cost as a result of suspending work (or reducing the rate of work) in accordance with this Sub-Clause, the Seller shall give notice to the Buyer and shall be entitled to an extension of time for any such delay, if completion is or will be delayed and payment of any such Cost, which shall be included in the Contract Price to Buyer. If the suspension under this Sub-Clause continues for a continues period of 60 days then the Seller may, upon giving 14 days' notice to the Buyer, terminate the Contract. Upon such termination, Seller shall be entitled to payment of amounts for the works already carried out and all other incidental costs incurred including costs of material already ordered or under production, cost of demobilizing and liabilities due to vendors and sub-contractors of the Seller." | As per Tender
27 | SLD | Kindly confirm the location of the Existing LT Panel & also confirm the cable between existing LT panel to New changeover panel is in whose scope. | Refer Clause no 7.2
28 | SLD | Kindly confirm the location of the New changeover panel which is indicated as substation room, but in layout the substatin room is not located. | Refer drawing provided
29 | Site Plan & DC Area | Kindly confirm the new cable route indicated need to be created new trench / hume pipe or a existing available. | Refer Site layout drawing and cabe should be burried
30 | SLD UPS-75 KVA Module size - 25 / 30 KW with 3 working and 1 stand by | Kindly confirm can we propose 2 Working & 1 Standby module, 2 working module capacity is more than 75 kVA. | As per Tender
31 | Page 40 / Clause 7.10 Stainless steel (SS) cable tray to be considered above each row of the Rack along with required Cable tray Grid above the rack and below false ceiling to be considered and provided. Refer Layout Drawing. SS Cable tray are used to run fiber and interconnecting cables.Rack Interconnecting cables mostly will be fiber, Bidder to take care utmost care as 90 Deg C bend will not be accepted. | Kindly confirm no of Tier cable tray required for networking. | Single Tier
32 | page 21/clause 2 BMS monitoring of CDU | Pls let us know total how many soft points to be considerde as well as what type of communication protocol between CDU to BMS | MODBUS SNMP - 35 nos of soft IO to be considered per CDU
33 | page 54/96 split units for UPS/Battery room | wall mounted split units of 11 kw (3.127 TR) may not be available with OEM's. Kindly review and modify the ratings | As per Tender
34 | page 59/96 water storage tanks -SMC Panel construction | Kindly review the requirement of 8000 liters also is it possible to go for multiple cylindrical tanks of say 4kLiters | We prefer to go with single tank , however bidder can choose between 1 X 8000 liters or 2 X 4000 liters
35 | page 29/36 1 X 75 KVA UPS for NON-IT Load – Utiliy Load with SMF batteries for 10 minutes back up time 0n 75 KVA. (Module Size should be 25KW or 30 KW– 3 numbers working and 1 standby module in same frame) | We can provide 40 KW module with – 2 Working + 1 Standby | As per Tender. UPS modules should be 3 nos. working and 1 nos standby
36 | page 31/96 Overload Rating Online-125% - 1 minute; 150% - 60 Sec | 150%-60 Sec, 120%-10 min as per market standards | OK
37 | page 37/96 Capablity to parallel 6 similar ups systems | Parallel upto 4 similar UPS's. | Accepted
38 | page 61/96 Clause 9.2.5 BMS should control the operation of oxygen pumping equipment’s i.e. In ROw under fire situation. | Oxygen pumping equipment i.e inrow shall be connecte to Fire alarm panel to shutdown equipment when a fire alarm is triggered. Please confirm. | Correct Not only IN row but AC in the Battery room also needs to shut down.
39 | page 63/96 Clause 9.6 WLD | Please confirm areas/Rooms to be covered by WLD | Server Room and UPS and Battery Room
40 | page 63/96 Clause 9.5 Rodent System | Please confirm areas/Rooms to be covered by Rodent system | Server Room and UPS and Battery Room
41 | page 64/96 Clause 9.7 Suppression system needs to be inside the server rack as system is with close containment and in UPS and battery room needs to be for full room. | As per the layout hot aisle is contained, and both cold aisle sides are open. As per guidelines fire suppression system needs to be for full room for server area. Fire suppression sysem Nozzle shall be provided for hot aisle containment. Please confirm. | As per drawing provided . Drawing are provided with only Hot aisel containtement . Gas supression system needs to be considered for entire server area and entire UPS and Battery area.